Din Rail Multifunction Meter Register Map

Ver. 1.0 (24.06.2022)

Procom Meters MODBUS Specifications Version 1.0.

Protocol	MODBUS RTU (RS485)

Data bits	8

Baud rate	Default: 9600 Baud

Setting: 1200/2400/4800/9600/19200

Parity	Default: None

Setting: Even/Odd/None

Device Address	Default: 1 Setting: 1-247

Stop bit	Default: 1

Setting: 1 or 2

Function Code	03H (Read),10H(Write)

Data type	32 Bit Unsigned 32 Bit float

The communication from meter is "Big Endian" that is, the more significant byte of a value is sent before the less significant byte.

All parameters can be read as individual or block. The Parameter address table is generalized table for all PROCOM Meters. The availability of the parameters is model dependent, please refer to the product catalog for the parameters available. If the parameter is not available then a value of '0' (zero) is sent through the meter. As all parameters are in 32bits, so length 1 is not allowed.

It is recommended to use twisted pair shielded cable for RS485 Communication and a good quality data converter, RS485 to RS232 and USB to Serial, if being used. A termination resistance of 120 ohm is recommended at the terminals of cable as per RS485 specifications.

| Basic Channel Parameters: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Parameter | Address | Data Type | No. Of Bytes | Unit |
| Voltage Phase1 to N, VR | 41003 | Float | 4 | Volts |
| Voltage Phase2 to N, VY | 41005 | Float | 4 | Volts |
| Voltage Phase3 to N, VB | 41007 | Float | 4 | Volts |
| Voltage Phase1 to Phase2, VRY | 41009 | Float | 4 | Volts |
| Voltage Phase2 to Phase3, VYB | 41011 | Float | 4 | Volts |
| Voltage Phase3 to Phase1, VBR | 41013 | Float | 4 | Volts |
| Current Phase1, IR | 41015 | Float | 4 | Amp |
| Current Phase2, IY | 41017 | Float | 4 | Amp |
| Current Phase3, IB | 41019 | Float | 4 | Amp |
| Current Neutral, IN | 41021 | Float | 4 | Amp |
| Power Phase1, WR | 41023 | Float | 4 | Watt |
| Power Phase2, WY | 41025 | Float | 4 | Watt |
| Power Phase3, WB | 41027 | Float | 4 | Watt |
| Sum Power, WT | 41029 | Float | 4 | Watt |
| Apparent Power Phase1, VAR | 41039 | Float | 4 | VA |
| Apparent Power Phase2, VAY | 41041 | Float | 4 | VA |
| Apparent Power Phase3, VAB | 41043 | Float | 4 | VA |
| Total Apparent Power, VAT | 41045 | Float | 4 | VA |
| Reactive Power Phase1, VARR | 41047 | Float | 4 | VAR |
| Reactive Power Phase2, VARY | 41049 | Float | 4 | VAR |
| Reactive Power Phase3, VARB | 41051 | Float | 4 | VAR |
| Total Reactive Power, VART | 41053 | Float | 4 | VAR |
| Power Factor Phase1, PFR | 41055 | Float | 4 |  |
| Power Factor Phase2, PFY | 41057 | Float | 4 |  |
| Power Factor Phase3, PFB | 41059 | Float | 4 |  |
| Total Power Factor, PFT | 41061 | Float | 4 |  |
| Frequency, F | 41063 | Float | 4 | Hz |
| Average Current | 41079 | Float | 4 | Amp |
| Current Unbalance | 41081 | Float | 4 | In % |
| Voltage Unbalance | 41083 | Float | 4 | In % |
| Angle Phase1, ӨR | 41085 | Float | 4 | Degree |
| Angle Phase2, ӨY | 41087 | Float | 4 | Degree |
| Angle Phase3, ӨB | 41089 | Float | 4 | Degree |

| Energy Import Block: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Parameter | Address | Data Type | No. Of Bytes | Unit |
| Load Hour | 42103 | Long | 4 | In seconds |
| Energy | 42105 | Float | 4 | Wh |
| Apparent Energy | 42107 | Float | 4 | VAH |
| Reactive Energy +ve | 42109 | Float | 4 | VARH |
| Reactive Energy -ve | 42111 | Float | 4 | VARH |
| Interruptions | 42113 | Long | 4 | Numbers |

| Energy Old Import Block: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Parameter | Address | Data Type | No. Of Bytes | Unit |
| Load Hour | 42303 | Long | 4 | In seconds |
| Energy | 42305 | Float | 4 | Wh |
| Apparent Energy | 42307 | Float | 4 | VAH |
| Reactive Energy +ve | 42309 | Float | 4 | VARH |
| Reactive Energy -ve | 42311 | Float | 4 | VARH |
| Interruptions | 42313 | Long | 4 | Numbers |

| Password Verify for Edit Parameters: | Function Code : Write:0x10H |  |  |  |
| --- | --- | --- | --- | --- |
| Parameter | Address | Data Type | No. Of Bytes | Unit |
| Password | 4100 | Long | 4 | value(0-999) |

| Editable Parameters : | Function Code Read :0x03H / Write:0x10H |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Parameter | Address |  | Data Type | No. Of Bytes |  | Unit |
| PT Primary Value |  | 5001 | Long | 4 | Volts(50 - 999) |  |
| PT Primary Decimal |  | 5003 | Long | 4 | 0,1,2(decimal point) |  |
| PT Primary unit |  | 5005 | Long | 4 | 0,1(default,K) |  |
| PT Secondary Value |  | 5007 | Long | 4 | Volts(50 – 999) |  |
| CT Primary Value |  | 5009 | Long | 4 | Volts(1 - 999) |  |
| CT Primary Decimal |  | 5011 | Long | 4 | 0,1,2(decimal point) |  |
| CT Primary unit |  | 5013 | Long | 4 | 0,1(default,K) |  |
| CT Secondary Value |  | 5015 | Long | 4 | Volts(1-10) |  |
| System Config |  | 5017 | Long | 4 | 0,1,2(3p4w,3p3w,1p) |  |
| KVA Type |  | 5019 | Long | 4 | 0,1(3D,Arth) |  |
| Starting Current |  | 5021 | Long | 4 | Amps(1-200) |  |
| Reserved |  | 5023 | Long | 4 |  |  |
| Reserved |  | 5025 | Long | 4 |  |  |
| Device ID |  | 5027 | Long | 4 | Number(1-247) |  |
| Baud Rate |  | 5029 | Long | 4 | 0,1,2,3,4(1200,2400,4800,9600,9200) |  |
| Parity |  | 5031 | Long | 4 | 0,1,2(None,Even,Odd) |  |
| Stop Bit |  | 5033 | Long | 4 | 0,1(1,2) |  |
| Endian Type |  | 5035 | Long | 4 | 0,1(Big,Lit) |  |