## Customer Modbus Table
Controller: | SOCO
Firmware | V2.15
Protocol | Modbus RTU (RS485)
Addresses | 1-Based Addressing
Parameters | Units of | Data Type | Size in byte | Conversion | Type of Register | Modbus | No. of | Remarks
| Measurement | (Float/Hex etc.) |  | Multiplier to read the data |  | Register Address | Registers required
READ MULTIPLE HOLDING REGISTER (Function Code: 0x03)
Grid Voltage Phase1 to N | Volts | Float | 4 | 1 | Holding Register | 1003 | 2
Grid Voltage Phase2 to N | Volts | Float | 4 | 1 | Holding Register | 1005 | 2
Grid Voltage Phase3 to N | Volts | Float | 4 | 1 | Holding Register | 1007 | 2
Grid Voltage Phase1 to Phase2 | Volts | Float | 4 | 1 | Holding Register | 1009 | 2
Grid Voltage Phase2 to Phase3 | Volts | Float | 4 | 1 | Holding Register | 1011 | 2
Grid Voltage Phase3 to Phase1 | Volts | Float | 4 | 1 | Holding Register | 1013 | 2
Grid Current Phase1 | Ampere | Float | 4 | 1 | Holding Register | 1015 | 2
Grid Current Phase2 | Ampere | Float | 4 | 1 | Holding Register | 1017 | 2
Grid Current Phase3 | Ampere | Float | 4 | 1 | Holding Register | 1019 | 2
Grid Current Neutral | Ampere | Float | 4 | 1 | Holding Register | 1021 | 2
Grid Power Phase1 | Watt | Float | 4 | 1 | Holding Register | 1023 | 2
Grid Power Phase2 | Watt | Float | 4 | 1 | Holding Register | 1025 | 2
Grid Power Phase3 | Watt | Float | 4 | 1 | Holding Register | 1027 | 2
Grid Sum Power | Watt | Float | 4 | 1 | Holding Register | 1029 | 2
Grid Apparent Power Phase1 | VA | Float | 4 | 1 | Holding Register | 1039 | 2
Grid Apparent Power Phase2 | VA | Float | 4 | 1 | Holding Register | 1041 | 2
Grid Apparent Power Phase3 | VA | Float | 4 | 1 | Holding Register | 1043 | 2
Grid Total Apparent Power | VA | Float | 4 | 1 | Holding Register | 1045 | 2
Grid Reactive Power Phase1 | VAR | Float | 4 | 1 | Holding Register | 1047 | 2
Grid Reactive Power Phase2 | VAR | Float | 4 | 1 | Holding Register | 1049 | 2
Grid Reactive Power Phase3 | VAR | Float | 4 | 1 | Holding Register | 1051 | 2
Grid Total Reactive Power | VAR | Float | 4 | 1 | Holding Register | 1053 | 2
Grid Power Factor Phase1 | NA | Float | 4 | 1 | Holding Register | 1055 | 2
Grid Power Factor Phase2 | NA | Float | 4 | 1 | Holding Register | 1057 | 2
Grid Power Factor Phase3 | NA | Float | 4 | 1 | Holding Register | 1059 | 2
Grid Total Power Factor | NA | Float | 4 | 1 | Holding Register | 1061 | 2
Grid R Phase Frequency | NA | Float | 4 | 1 | Holding Register | 1201 | 2
Grid Y Phase Frequency | NA | Float | 4 | 1 | Holding Register | 1203 | 2
Grid B Phase Frequency | NA | Float | 4 | 1 | Holding Register | 1205 | 2
Grid Import Energy | Wh | Float | 4 | 1 | Holding Register | 2105 | 2
Grid Import Apparent Energy | VAH | Float | 4 | 1 | Holding Register | 2107 | 2
Grid Import Reactive Energy +ve | VARH | Float | 4 | 1 | Holding Register | 2109 | 2
Grid Import Reactive Energy -ve | VARH | Float | 4 | 1 | Holding Register | 2111 | 2
Grid Export Energy | Wh | Float | 4 | 1 | Holding Register | 2205 | 2
Grid Export Apparent Energy | VAH | Float | 4 | 1 | Holding Register | 2207 | 2
Grid Export Reactive Energy +ve | VARH | Float | 4 | 1 | Holding Register | 2209 | 2
Grid Export Reactive Energy -ve | VARH | Float | 4 | 1 | Holding Register | 2211 | 2
Disable Load On Grid Duration Remaining | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 6001 | 2 | Number of seconds till Load Can't be put on Grid
Solar Voltage Phase1 to N | Volts | Float | 4 | 1 | Holding Register | 11003 | 2
Solar Voltage Phase2 to N | Volts | Float | 4 | 1 | Holding Register | 11005 | 2
Solar Voltage Phase3 to N | Volts | Float | 4 | 1 | Holding Register | 11007 | 2
Solar Voltage Phase1 to Phase2 | Volts | Float | 4 | 1 | Holding Register | 11009 | 2
Solar Voltage Phase2 to Phase3 | Volts | Float | 4 | 1 | Holding Register | 11011 | 2
Solar Voltage Phase3 to Phase1 | Volts | Float | 4 | 1 | Holding Register | 11013 | 2
Solar Current Phase1 | Ampere | Float | 4 | 1 | Holding Register | 11015 | 2
Solar Current Phase2 | Ampere | Float | 4 | 1 | Holding Register | 11017 | 2
Solar Current Phase3 | Ampere | Float | 4 | 1 | Holding Register | 11019 | 2
Solar Current Neutral | Ampere | Float | 4 | 1 | Holding Register | 11021 | 2
Solar Power Phase1 | Watt | Float | 4 | 1 | Holding Register | 11023 | 2
Solar Power Phase2 | Watt | Float | 4 | 1 | Holding Register | 11025 | 2
Solar Power Phase3 | Watt | Float | 4 | 1 | Holding Register | 11027 | 2
Solar Sum Power | Watt | Float | 4 | 1 | Holding Register | 11029 | 2
Solar Apparent Power Phase1 | VA | Float | 4 | 1 | Holding Register | 11039 | 2
Solar Apparent Power Phase2 | VA | Float | 4 | 1 | Holding Register | 11041 | 2
Solar Apparent Power Phase3 | VA | Float | 4 | 1 | Holding Register | 11043 | 2
Solar Total Apparent Power | VA | Float | 4 | 1 | Holding Register | 11045 | 2
Solar Reactive Power Phase1 | VAR | Float | 4 | 1 | Holding Register | 11047 | 2
Solar Reactive Power Phase2 | VAR | Float | 4 | 1 | Holding Register | 11049 | 2
Solar Reactive Power Phase3 | VAR | Float | 4 | 1 | Holding Register | 11051 | 2
Solar Total Reactive Power | VAR | Float | 4 | 1 | Holding Register | 11053 | 2
Solar Power Factor Phase1 | NA | Float | 4 | 1 | Holding Register | 11055 | 2
Solar Power Factor Phase2 | NA | Float | 4 | 1 | Holding Register | 11057 | 2
Solar Power Factor Phase3 | NA | Float | 4 | 1 | Holding Register | 11059 | 2
Solar Total Power Factor | NA | Float | 4 | 1 | Holding Register | 11061 | 2
Solar R Phase Frequency | NA | Float | 4 | 1 | Holding Register | 11201 | 2
Solar Y Phase Frequency | NA | Float | 4 | 1 | Holding Register | 11203 | 2
Solar B Phase Frequency | NA | Float | 4 | 1 | Holding Register | 11205 | 2
Solar Import Energy | Wh | Float | 4 | 1 | Holding Register | 12105 | 2
Solar Import Apparent Energy | VAH | Float | 4 | 1 | Holding Register | 12107 | 2
Solar Import Reactive Energy +ve | VARH | Float | 4 | 1 | Holding Register | 12109 | 2
Solar Import Reactive Energy -ve | VARH | Float | 4 | 1 | Holding Register | 12111 | 2
Solar Export Energy | Wh | Float | 4 | 1 | Holding Register | 12205 | 2
Solar Export Apparent Energy | VAH | Float | 4 | 1 | Holding Register | 12207 | 2
Solar Export Reactive Energy +ve | VARH | Float | 4 | 1 | Holding Register | 12209 | 2
Solar Export Reactive Energy -ve | VARH | Float | 4 | 1 | Holding Register | 12211 | 2
Disable Load On Solar Duration Remaining | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 16001 | 2 | Number of seconds till Load Can't be put on Solar
Fan 1 Current | Ampere | Float | 4 | 1 | Holding Register | 20001 | 2
Fan 2 Current | Ampere | Float | 4 | 1 | Holding Register | 20003 | 2
Ambient Temperature | Celsius | Float | 4 | 1 | Holding Register | 20005 | 2
Mains Under Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30001 | 2
Mains Over Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30003 | 2
Mains Under Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30005 | 2
Mains Over Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30007 | 2
Mains Fail Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30009 | 2
Mains Return Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30011 | 2
Solar Under Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30013 | 2
Solar Over Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30015 | 2
Solar Under Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30017 | 2
Solar Over Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30019 | 2
Solar Fail Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30021 | 2
Solar Return Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30023 | 2
Fan Under Current Setting | Milli Ampere | Unsigned Integer | 4 | 1 | Holding Register | 30025 | 2
Fan Over Current Setting | Milli Ampere | Unsigned Integer | 4 | 1 | Holding Register | 30027 | 2
Over Temperature Setting | Celsius | Unsigned Integer | 4 | 1 | Holding Register | 30029 | 2
Under Temperature Setting | Celsius | Unsigned Integer | 4 | 1 | Holding Register | 30031 | 2
Over Temperature Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30033 | 2
Under Temperature Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30035 | 2
DG Detection Disable Setting | NA | Unsigned Integer | 4 | 1 | Holding Register | 30037 | 2 | 0: OFF (DG Detection Enabled), 1: ON (DG Detection Disabled)
Fan Disable Setting | NA | Unsigned Integer | 4 | 1 | Holding Register | 30039 | 2 | 0: OFF (Fans Enabled), 1: ON (Fans Disabled)
Firmware Upgrade Status | NA | Unsigned Integer | 4 | 1 | Holding Register | 40001 | 2 | 0: No Firmware Upgrade Ongoing/Firmware Upgrade completed, 1:Firmware Uploading Ongoing, 2: Firmware Updating Ongoing, 127: Error Occured
Serial Number Lower Half | NA | Unsigned Integer | 4 | 1 | Holding Register | 50003 | 2
Serial Number Upper Half | NA | Unsigned Integer | 4 | 1 | Holding Register | 50005 | 2
Version Number | NA | Unsigned Integer | 4 | 0.01 | Holding Register | 50007 | 2
Parameters | Units of | Data Type | Size in byte | Conversion | Type of Register | Modbus | No. of | Remarks
| Measurement | (Float/Hex etc.) |  | Multiplier to read the data |  | Register Address | Registers required
READ INPUT STATUS (Function Code: 0x02)
Grid Phase 1 Contactor On Feedback | NA | BIT | NA | NA | Input Status | 1 | 1
Grid Phase 2 Contactor On Feedback | NA | BIT | NA | NA | Input Status | 2 | 1
Grid Phase 3 Contactor On Feedback | NA | BIT | NA | NA | Input Status | 3 | 1
Load On Solar Contactor On Feedback | NA | BIT | NA | NA | Input Status | 4 | 1
Load On Grid Contactor On Feedback | NA | BIT | NA | NA | Input Status | 5 | 1
Solar Neutral Earth Contactor On Feedback | NA | BIT | NA | NA | Input Status | 6 | 1
DG Off | NA | BIT | NA | NA | Input Status | 7 | 1
Reserved | NA | BIT | NA | NA | Input Status | 8 | 1
DC Aux Power Available | NA | BIT | NA | NA | Input Status | 201 | 1
AC Aux Power Available | NA | BIT | NA | NA | Input Status | 202 | 1
Grid R Phase Under Voltage | NA | BIT | NA | NA | Input Status | 301 | 1
Grid R Phase Over Voltage | NA | BIT | NA | NA | Input Status | 302 | 1
Grid Y Phase Under Voltage | NA | BIT | NA | NA | Input Status | 303 | 1
Grid Y Phase Over Voltage | NA | BIT | NA | NA | Input Status | 304 | 1
Grid B Phase Under Voltage | NA | BIT | NA | NA | Input Status | 305 | 1
Grid B Phase Over Voltage | NA | BIT | NA | NA | Input Status | 306 | 1
Solar R Phase Under Voltage | NA | BIT | NA | NA | Input Status | 307 | 1
Solar R Phase Over Voltage | NA | BIT | NA | NA | Input Status | 308 | 1
Solar Y Phase Under Voltage | NA | BIT | NA | NA | Input Status | 309 | 1
Solar Y Phase Over Voltage | NA | BIT | NA | NA | Input Status | 310 | 1
Solar B Phase Under Voltage | NA | BIT | NA | NA | Input Status | 311 | 1
Solar B Phase Over Voltage | NA | BIT | NA | NA | Input Status | 312 | 1
Grid R Phase Loss | NA | BIT | NA | NA | Input Status | 313 | 1
Grid Y Phase Loss | NA | BIT | NA | NA | Input Status | 314 | 1
Grid B Phase Loss | NA | BIT | NA | NA | Input Status | 315 | 1
Solar R Phase Loss | NA | BIT | NA | NA | Input Status | 316 | 1
Solar Y Phase Loss | NA | BIT | NA | NA | Input Status | 317 | 1
Solar B Phase Loss | NA | BIT | NA | NA | Input Status | 318 | 1
Relay 1 Energized (Grid R Phase Contactor Coil Deenergized) | NA | BIT | NA | NA | Input Status | 401 | 1
Relay 2 Energized (Grid Y Phase Contactor Coil Deenergized) | NA | BIT | NA | NA | Input Status | 402 | 1
Relay 3 Energized (Grid B Phase Contactor Coil Deenergized) | NA | BIT | NA | NA | Input Status | 403 | 1
Relay 4 Energized (Load On Solar Contactor Coil Energized & Solar Neutral To Earth Contactor Coil Energized) | NA | BIT | NA | NA | Input Status | 404 | 1
Relay 5 Energized (Load On Grid Contactor Coil Deenergized) | NA | BIT | NA | NA | Input Status | 405 | 1
Relay 6 Energized (Fans Output Deenergized) | NA | BIT | NA | NA | Input Status | 406 | 1
Grid R Phase Contactor Stuck Open Error Suspected | NA | BIT | NA | NA | Input Status | 601 | 1
Grid R Phase Contactor Stuck Closed Error Suspected | NA | BIT | NA | NA | Input Status | 602 | 1
Grid Y Phase Contactor Stuck Open Error Suspected | NA | BIT | NA | NA | Input Status | 603 | 1
Grid Y Phase Contactor Stuck Closed Error Suspected | NA | BIT | NA | NA | Input Status | 604 | 1
Grid B Phase Contactor Stuck Open Error Suspected | NA | BIT | NA | NA | Input Status | 605 | 1
Grid B Phase Contactor Stuck Closed Error Suspected | NA | BIT | NA | NA | Input Status | 606 | 1
Load On Solar Contactor Stuck Open Error Suspected | NA | BIT | NA | NA | Input Status | 607 | 1
Load On Solar Contactor Stuck Closed Error Suspected | NA | BIT | NA | NA | Input Status | 608 | 1
Load On Grid Contactor Stuck Open Error Suspected | NA | BIT | NA | NA | Input Status | 609 | 1
Load On Grid Contactor Stuck Closed Error Suspected | NA | BIT | NA | NA | Input Status | 610 | 1
Solar Neutral Earth Contactor Stuck Open Error Suspected | NA | BIT | NA | NA | Input Status | 611 | 1
Solar Neutral Earth Contactor Stuck Closed Error Suspected | NA | BIT | NA | NA | Input Status | 612 | 1
Load On Grid | NA | BIT | NA | NA | Input Status | 801 | 1
Load Not On Grid As User Disabled | NA | BIT | NA | NA | Input Status | 802 | 1
Load Not On Grid As Grid R Phase Unhealthy | NA | BIT | NA | NA | Input Status | 803 | 1
Load Not On Grid As Solar Contactors On | NA | BIT | NA | NA | Input Status | 804 | 1
Load On Solar | NA | BIT | NA | NA | Input Status | 805 | 1
Load Not On Solar As User Disabled | NA | BIT | NA | NA | Input Status | 806 | 1
Load Not On Solar As Solar R Phase Unhealthy | NA | BIT | NA | NA | Input Status | 807 | 1
Load Not On Solar As Grid Contactors On | NA | BIT | NA | NA | Input Status | 808 | 1
Load Not On Solar As DG Running | NA | BIT | NA | NA | Input Status | 809 | 1
Fan 1 Short Circuit | NA | BIT | NA | NA | Input Status | 901 | 1
Fan 1 Open Circuit | NA | BIT | NA | NA | Input Status | 902 | 1
Fan 2 Short Circuit | NA | BIT | NA | NA | Input Status | 903 | 1
Fan 2 Open Circuit | NA | BIT | NA | NA | Input Status | 904 | 1
Parameters | Units of | Data Type | Size in byte | Conversion | Type of Register | Modbus | No. of | Remarks
| Measurement | (Float/Hex etc.) |  | Multiplier to read the data |  | Register Address | Registers required
WRITE MULTIPLE HOLDING REGISTERS (0x10)
Disable Load On Grid Duration Remaining | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 6001 | 2 | Number of seconds till Load Can't be put on Grid
Disable Load On Solar Duration Remaining | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 16001 | 2 | Number of seconds till Load Can't be put on Solar
Mains Under Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30001 | 2
Mains Over Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30003 | 2
Mains Under Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30005 | 2
Mains Over Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30007 | 2
Mains Fail Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30009 | 2
Mains Return Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30011 | 2
Solar Under Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30013 | 2
Solar Over Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30015 | 2
Solar Under Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30017 | 2
Solar Over Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30019 | 2
Solar Fail Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30021 | 2
Solar Return Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30023 | 2
Fan Under Current Setting | Milli Ampere | Unsigned Integer | 4 | 1 | Holding Register | 30025 | 2
Fan Over Current Setting | Milli Ampere | Unsigned Integer | 4 | 1 | Holding Register | 30027 | 2
Over Temperature Setting | Celsius | Unsigned Integer | 4 | 1 | Holding Register | 30029 | 2
Under Temperature Setting | Celsius | Unsigned Integer | 4 | 1 | Holding Register | 30031 | 2
Over Temperature Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30033 | 2
Under Temperature Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30035 | 2
DG Detection Enable/Disable Setting | NA | Unsigned Integer | 4 | 1 | Holding Register | 30037 | 2 | 0: OFF (DG Detection Enabled), 1: ON (DG Detection Disabled)
Fan Disable Setting | NA | Unsigned Integer | 4 | 1 | Holding Register | 30039 | 2 | 0: OFF (Fans Enabled), 1: ON (Fans Disabled)
Firmware Upgrade Status | NA | Unsigned Integer | 4 | 1 | Holding Register | 40001 | 2 | 0: No Action, 1:Signals start of Firmware Uploading, 2: Signals end of Firmware Uploading

## Internal Modbus Table
Controller: | SOCO
Firmware | V2.15
Protocol | Modbus RTU (RS485)
Addresses | 1-Based Addressing
Parameters | Units of | Data Type | Size in byte | Conversion | Type of Register | Modbus | No. of | Remarks
| Measurement | (Float/Hex etc.) |  | Multiplier to read the data |  | Register Address | Registers required
READ MULTIPLE HOLDING REGISTER (Function Code: 0x03)
Grid Voltage Phase1 to N | Volts | Float | 4 | 1 | Holding Register | 1003 | 2
Grid Voltage Phase2 to N | Volts | Float | 4 | 1 | Holding Register | 1005 | 2
Grid Voltage Phase3 to N | Volts | Float | 4 | 1 | Holding Register | 1007 | 2
Grid Voltage Phase1 to Phase2 | Volts | Float | 4 | 1 | Holding Register | 1009 | 2
Grid Voltage Phase2 to Phase3 | Volts | Float | 4 | 1 | Holding Register | 1011 | 2
Grid Voltage Phase3 to Phase1 | Volts | Float | 4 | 1 | Holding Register | 1013 | 2
Grid Current Phase1 | Ampere | Float | 4 | 1 | Holding Register | 1015 | 2
Grid Current Phase2 | Ampere | Float | 4 | 1 | Holding Register | 1017 | 2
Grid Current Phase3 | Ampere | Float | 4 | 1 | Holding Register | 1019 | 2
Grid Current Neutral | Ampere | Float | 4 | 1 | Holding Register | 1021 | 2
Grid Power Phase1 | Watt | Float | 4 | 1 | Holding Register | 1023 | 2
Grid Power Phase2 | Watt | Float | 4 | 1 | Holding Register | 1025 | 2
Grid Power Phase3 | Watt | Float | 4 | 1 | Holding Register | 1027 | 2
Grid Sum Power | Watt | Float | 4 | 1 | Holding Register | 1029 | 2
Grid Apparent Power Phase1 | VA | Float | 4 | 1 | Holding Register | 1039 | 2
Grid Apparent Power Phase2 | VA | Float | 4 | 1 | Holding Register | 1041 | 2
Grid Apparent Power Phase3 | VA | Float | 4 | 1 | Holding Register | 1043 | 2
Grid Total Apparent Power | VA | Float | 4 | 1 | Holding Register | 1045 | 2
Grid Reactive Power Phase1 | VAR | Float | 4 | 1 | Holding Register | 1047 | 2
Grid Reactive Power Phase2 | VAR | Float | 4 | 1 | Holding Register | 1049 | 2
Grid Reactive Power Phase3 | VAR | Float | 4 | 1 | Holding Register | 1051 | 2
Grid Total Reactive Power | VAR | Float | 4 | 1 | Holding Register | 1053 | 2
Grid Power Factor Phase1 | NA | Float | 4 | 1 | Holding Register | 1055 | 2
Grid Power Factor Phase2 | NA | Float | 4 | 1 | Holding Register | 1057 | 2
Grid Power Factor Phase3 | NA | Float | 4 | 1 | Holding Register | 1059 | 2
Grid Total Power Factor | NA | Float | 4 | 1 | Holding Register | 1061 | 2
Grid R Phase Frequency | NA | Float | 4 | 1 | Holding Register | 1201 | 2
Grid Y Phase Frequency | NA | Float | 4 | 1 | Holding Register | 1203 | 2
Grid B Phase Frequency | NA | Float | 4 | 1 | Holding Register | 1205 | 2
Grid Import Energy | Wh | Float | 4 | 1 | Holding Register | 2105 | 2
Grid Import Apparent Energy | VAH | Float | 4 | 1 | Holding Register | 2107 | 2
Grid Import Reactive Energy +ve | VARH | Float | 4 | 1 | Holding Register | 2109 | 2
Grid Import Reactive Energy -ve | VARH | Float | 4 | 1 | Holding Register | 2111 | 2
Grid Export Energy | Wh | Float | 4 | 1 | Holding Register | 2205 | 2
Grid Export Apparent Energy | VAH | Float | 4 | 1 | Holding Register | 2207 | 2
Grid Export Reactive Energy +ve | VARH | Float | 4 | 1 | Holding Register | 2209 | 2
Grid Export Reactive Energy -ve | VARH | Float | 4 | 1 | Holding Register | 2211 | 2
Disable Load On Grid Duration Remaining | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 6001 | 2 | Number of seconds till Load Can't be put on Grid
Solar Voltage Phase1 to N | Volts | Float | 4 | 1 | Holding Register | 11003 | 2
Solar Voltage Phase2 to N | Volts | Float | 4 | 1 | Holding Register | 11005 | 2
Solar Voltage Phase3 to N | Volts | Float | 4 | 1 | Holding Register | 11007 | 2
Solar Voltage Phase1 to Phase2 | Volts | Float | 4 | 1 | Holding Register | 11009 | 2
Solar Voltage Phase2 to Phase3 | Volts | Float | 4 | 1 | Holding Register | 11011 | 2
Solar Voltage Phase3 to Phase1 | Volts | Float | 4 | 1 | Holding Register | 11013 | 2
Solar Current Phase1 | Ampere | Float | 4 | 1 | Holding Register | 11015 | 2
Solar Current Phase2 | Ampere | Float | 4 | 1 | Holding Register | 11017 | 2
Solar Current Phase3 | Ampere | Float | 4 | 1 | Holding Register | 11019 | 2
Solar Current Neutral | Ampere | Float | 4 | 1 | Holding Register | 11021 | 2
Solar Power Phase1 | Watt | Float | 4 | 1 | Holding Register | 11023 | 2
Solar Power Phase2 | Watt | Float | 4 | 1 | Holding Register | 11025 | 2
Solar Power Phase3 | Watt | Float | 4 | 1 | Holding Register | 11027 | 2
Solar Sum Power | Watt | Float | 4 | 1 | Holding Register | 11029 | 2
Solar Apparent Power Phase1 | VA | Float | 4 | 1 | Holding Register | 11039 | 2
Solar Apparent Power Phase2 | VA | Float | 4 | 1 | Holding Register | 11041 | 2
Solar Apparent Power Phase3 | VA | Float | 4 | 1 | Holding Register | 11043 | 2
Solar Total Apparent Power | VA | Float | 4 | 1 | Holding Register | 11045 | 2
Solar Reactive Power Phase1 | VAR | Float | 4 | 1 | Holding Register | 11047 | 2
Solar Reactive Power Phase2 | VAR | Float | 4 | 1 | Holding Register | 11049 | 2
Solar Reactive Power Phase3 | VAR | Float | 4 | 1 | Holding Register | 11051 | 2
Solar Total Reactive Power | VAR | Float | 4 | 1 | Holding Register | 11053 | 2
Solar Power Factor Phase1 | NA | Float | 4 | 1 | Holding Register | 11055 | 2
Solar Power Factor Phase2 | NA | Float | 4 | 1 | Holding Register | 11057 | 2
Solar Power Factor Phase3 | NA | Float | 4 | 1 | Holding Register | 11059 | 2
Solar Total Power Factor | NA | Float | 4 | 1 | Holding Register | 11061 | 2
Solar R Phase Frequency | NA | Float | 4 | 1 | Holding Register | 11201 | 2
Solar Y Phase Frequency | NA | Float | 4 | 1 | Holding Register | 11203 | 2
Solar B Phase Frequency | NA | Float | 4 | 1 | Holding Register | 11205 | 2
Solar Import Energy | Wh | Float | 4 | 1 | Holding Register | 12105 | 2
Solar Import Apparent Energy | VAH | Float | 4 | 1 | Holding Register | 12107 | 2
Solar Import Reactive Energy +ve | VARH | Float | 4 | 1 | Holding Register | 12109 | 2
Solar Import Reactive Energy -ve | VARH | Float | 4 | 1 | Holding Register | 12111 | 2
Solar Export Energy | Wh | Float | 4 | 1 | Holding Register | 12205 | 2
Solar Export Apparent Energy | VAH | Float | 4 | 1 | Holding Register | 12207 | 2
Solar Export Reactive Energy +ve | VARH | Float | 4 | 1 | Holding Register | 12209 | 2
Solar Export Reactive Energy -ve | VARH | Float | 4 | 1 | Holding Register | 12211 | 2
Disable Load On Solar Duration Remaining | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 16001 | 2 | Number of seconds till Load Can't be put on Solar
Fan 1 Current | Ampere | Float | 4 | 1 | Holding Register | 20001 | 2
Fan 2 Current | Ampere | Float | 4 | 1 | Holding Register | 20003 | 2
Ambient Temperature | Celsius | Float | 4 | 1 | Holding Register | 20005 | 2
Mains Under Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30001 | 2
Mains Over Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30003 | 2
Mains Under Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30005 | 2
Mains Over Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30007 | 2
Mains Fail Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30009 | 2
Mains Return Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30011 | 2
Solar Under Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30013 | 2
Solar Over Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30015 | 2
Solar Under Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30017 | 2
Solar Over Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30019 | 2
Solar Fail Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30021 | 2
Solar Return Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30023 | 2
Fan Under Current Setting | Milli Ampere | Unsigned Integer | 4 | 1 | Holding Register | 30025 | 2
Fan Over Current Setting | Milli Ampere | Unsigned Integer | 4 | 1 | Holding Register | 30027 | 2
Over Temperature Setting | Celsius | Unsigned Integer | 4 | 1 | Holding Register | 30029 | 2
Under Temperature Setting | Celsius | Unsigned Integer | 4 | 1 | Holding Register | 30031 | 2
Over Temperature Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30033 | 2
Under Temperature Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30035 | 2
DG Detection Disable Setting | NA | Unsigned Integer | 4 | 1 | Holding Register | 30037 | 2 | 0: OFF (DG Detection Enabled), 1: ON (DG Detection Disabled)
Fan Disable Setting | NA | Unsigned Integer | 4 | 1 | Holding Register | 30039 | 2 | 0: OFF (Fans Enabled), 1: ON (Fans Disabled)
Firmware Upgrade Status | NA | Unsigned Integer | 4 | 1 | Holding Register | 40001 | 2 | 0: No Firmware Upgrade Ongoing/Firmware Upgrade completed, 1:Firmware Uploading Ongoing, 2: Firmware Updating Ongoing, 127: Error Occured
Switch Pressed | NA | Unsigned Integer | 4 | 1 | Holding Register | 50001 | 2 | Internal Only. Not visible to customer. 1: “Next” Switch Pressed 2: “Decrement” Switch Pressed 3: “Next” & “Decrement” Switch Pressed 4: “Increment” Switch Pressed 5: “Next” & “Increment” Switch Pressed 6: “Increment” & “Decrement” Switch Pressed 7: “Next“, “Decrement” & “Increment” Switch Pressed
Serial Number Lower Half | NA | Unsigned Integer | 4 | 1 | Holding Register | 50003 | 2
Serial Number Upper Half | NA | Unsigned Integer | 4 | 1 | Holding Register | 50005 | 2
Version Number | NA | Unsigned Integer | 4 | 0.01 | Holding Register | 50007 | 2
Functionally Tested | NA | Unsigned Integer | 4 | 1 | Holding Register | 50009 | 2 | Internal Only. Not visible to customer. If set to non-zero, indicates product was tested functionally during production
Calibrated | NA | Unsigned Integer | 4 | 1 | Holding Register | 50011 | 2 | Internal Only. Not visible to customer. If set to non-zero, indicates product was calibrated during production
Calibration State | NA | Unsigned Integer | 4 | 1 | Holding Register | 50013 | 2 | Internal Only. Not visible to customer. Indicates the state machine of calibration 0: Calibration Not Initiated. Set Grid R/Y/B and Solar R/Y/B Voltages to 240V. Set Grid R/Y/B and Solar R/Y/B current to 100A. Set Grid R/Y/B and Solar R/Y/B Power Factor to 0.5. And then set Advance Calibration Flag. 17,18,19,20: Extra-High Point Calibration In Progress (V/I + PF at 100A) 21: Extra-High Point Calibration Done. Set Grid R/Y/B and Solar R/Y/B Voltages to 240V. Set Grid R/Y/B and Solar R/Y/B current to 20A. Set Grid R/Y/B and Solar R/Y/B Power Factor to 0.5. And then set Advance Calibration Flag. 22,23,24: High Point Calibration In Progress 25: High Point Calibration Done. Set Grid R/Y/B and Solar R/Y/B Voltages to 240V. Set Grid R/Y/B and Solar R/Y/B current to 4A. Set Grid R/Y/B and Solar R/Y/B Power Factor to 0.5. And then set Advance Calibration Flag. 26,27,28: Mid Point Calibration In Progress 29: Mid Point Calibration Done. Set Grid R/Y/B and Solar R/Y/B Voltages to 240V. Set Grid R/Y/B and Solar R/Y/B current to 0.4A. Set Grid R/Y/B and Solar R/Y/B Power Factor to 0.5. And then set Advance Calibration Flag. 30,31,32: Low Point Calibration In Progress 33: Low Point Calibration Done. Set Fan 1 Current and Fan 2 Current to 0.1A each. And then set Advance Calibration Flag. 34: Fan Calibration In Progress 127: Calibration Completed Successfully 126: Error occured during calibration. Please restart controller
Scratch Pad | NA | Unsigned Integer | 4 | 1 | Holding Register | 50015 | 2 | Internal Only. Not visible to customer. Used to store a temporarily value. Resets when SOCO restarts on POR.
Parameters | Units of | Data Type | Size in byte | Conversion | Type of Register | Modbus | No. of | Remarks
| Measurement | (Float/Hex etc.) |  | Multiplier to read the data |  | Register Address | Registers required
READ INPUT STATUS (Function Code: 0x02)
Grid Phase 1 Contactor On Feedback | NA | BIT | NA | NA | Input Status | 1 | 1
Grid Phase 2 Contactor On Feedback | NA | BIT | NA | NA | Input Status | 2 | 1
Grid Phase 3 Contactor On Feedback | NA | BIT | NA | NA | Input Status | 3 | 1
Load On Solar Contactor On Feedback | NA | BIT | NA | NA | Input Status | 4 | 1
Load On Grid Contactor On Feedback | NA | BIT | NA | NA | Input Status | 5 | 1
Solar Neutral Earth Contactor On Feedback | NA | BIT | NA | NA | Input Status | 6 | 1
DG Off | NA | BIT | NA | NA | Input Status | 7 | 1
Reserved | NA | BIT | NA | NA | Input Status | 8 | 1
DC Aux Power Available | NA | BIT | NA | NA | Input Status | 201 | 1
AC Aux Power Available | NA | BIT | NA | NA | Input Status | 202 | 1
Grid R Phase Under Voltage | NA | BIT | NA | NA | Input Status | 301 | 1
Grid R Phase Over Voltage | NA | BIT | NA | NA | Input Status | 302 | 1
Grid Y Phase Under Voltage | NA | BIT | NA | NA | Input Status | 303 | 1
Grid Y Phase Over Voltage | NA | BIT | NA | NA | Input Status | 304 | 1
Grid B Phase Under Voltage | NA | BIT | NA | NA | Input Status | 305 | 1
Grid B Phase Over Voltage | NA | BIT | NA | NA | Input Status | 306 | 1
Solar R Phase Under Voltage | NA | BIT | NA | NA | Input Status | 307 | 1
Solar R Phase Over Voltage | NA | BIT | NA | NA | Input Status | 308 | 1
Solar Y Phase Under Voltage | NA | BIT | NA | NA | Input Status | 309 | 1
Solar Y Phase Over Voltage | NA | BIT | NA | NA | Input Status | 310 | 1
Solar B Phase Under Voltage | NA | BIT | NA | NA | Input Status | 311 | 1
Solar B Phase Over Voltage | NA | BIT | NA | NA | Input Status | 312 | 1
Grid R Phase Loss | NA | BIT | NA | NA | Input Status | 313 | 1
Grid Y Phase Loss | NA | BIT | NA | NA | Input Status | 314 | 1
Grid B Phase Loss | NA | BIT | NA | NA | Input Status | 315 | 1
Solar R Phase Loss | NA | BIT | NA | NA | Input Status | 316 | 1
Solar Y Phase Loss | NA | BIT | NA | NA | Input Status | 317 | 1
Solar B Phase Loss | NA | BIT | NA | NA | Input Status | 318 | 1
Relay 1 Energized (Grid R Phase Contactor Coil Deenergized) | NA | BIT | NA | NA | Input Status | 401 | 1
Relay 2 Energized (Grid Y Phase Contactor Coil Deenergized) | NA | BIT | NA | NA | Input Status | 402 | 1
Relay 3 Energized (Grid B Phase Contactor Coil Deenergized) | NA | BIT | NA | NA | Input Status | 403 | 1
Relay 4 Energized (Load On Solar Contactor Coil Energized & Solar Neutral To Earth Contactor Coil Energized) | NA | BIT | NA | NA | Input Status | 404 | 1
Relay 5 Energized (Load On Grid Contactor Coil Deenergized) | NA | BIT | NA | NA | Input Status | 405 | 1
Relay 6 Energized (Fans Output Deenergized) | NA | BIT | NA | NA | Input Status | 406 | 1
Grid R Phase Contactor Stuck Open Error Suspected | NA | BIT | NA | NA | Input Status | 601 | 1
Grid R Phase Contactor Stuck Closed Error Suspected | NA | BIT | NA | NA | Input Status | 602 | 1
Grid Y Phase Contactor Stuck Open Error Suspected | NA | BIT | NA | NA | Input Status | 603 | 1
Grid Y Phase Contactor Stuck Closed Error Suspected | NA | BIT | NA | NA | Input Status | 604 | 1
Grid B Phase Contactor Stuck Open Error Suspected | NA | BIT | NA | NA | Input Status | 605 | 1
Grid B Phase Contactor Stuck Closed Error Suspected | NA | BIT | NA | NA | Input Status | 606 | 1
Load On Solar Contactor Stuck Open Error Suspected | NA | BIT | NA | NA | Input Status | 607 | 1
Load On Solar Contactor Stuck Closed Error Suspected | NA | BIT | NA | NA | Input Status | 608 | 1
Load On Grid Contactor Stuck Open Error Suspected | NA | BIT | NA | NA | Input Status | 609 | 1
Load On Grid Contactor Stuck Closed Error Suspected | NA | BIT | NA | NA | Input Status | 610 | 1
Solar Neutral Earth Contactor Stuck Open Error Suspected | NA | BIT | NA | NA | Input Status | 611 | 1
Solar Neutral Earth Contactor Stuck Closed Error Suspected | NA | BIT | NA | NA | Input Status | 612 | 1
Load On Grid | NA | BIT | NA | NA | Input Status | 801 | 1
Load Not On Grid As User Disabled | NA | BIT | NA | NA | Input Status | 802 | 1
Load Not On Grid As Grid R Phase Unhealthy | NA | BIT | NA | NA | Input Status | 803 | 1
Load Not On Grid As Solar Contactors On | NA | BIT | NA | NA | Input Status | 804 | 1
Load On Solar | NA | BIT | NA | NA | Input Status | 805 | 1
Load Not On Solar As User Disabled | NA | BIT | NA | NA | Input Status | 806 | 1
Load Not On Solar As Solar R Phase Unhealthy | NA | BIT | NA | NA | Input Status | 807 | 1
Load Not On Solar As Grid Contactors On | NA | BIT | NA | NA | Input Status | 808 | 1
Load Not On Solar As DG Running | NA | BIT | NA | NA | Input Status | 809 | 1
Fan 1 Short Circuit | NA | BIT | NA | NA | Input Status | 901 | 1
Fan 1 Open Circuit | NA | BIT | NA | NA | Input Status | 902 | 1
Fan 2 Short Circuit | NA | BIT | NA | NA | Input Status | 903 | 1
Fan 2 Open Circuit | NA | BIT | NA | NA | Input Status | 904 | 1
Parameters | Units of | Data Type | Size in byte | Conversion | Type of Register | Modbus | No. of | Remarks
| Measurement | (Float/Hex etc.) |  | Multiplier to read the data |  | Register Address | Registers required
READ COIL STATUS (Function Code: 0x01)
Digital Input 1 | NA | BIT | NA | NA | Coil Status | 20001 | 1 | Internal Only. Not visible to customer.
Digital Input 2 | NA | BIT | NA | NA | Coil Status | 20002 | 1 | Internal Only. Not visible to customer.
Digital Input 3 | NA | BIT | NA | NA | Coil Status | 20003 | 1 | Internal Only. Not visible to customer.
Digital Input 4 | NA | BIT | NA | NA | Coil Status | 20004 | 1 | Internal Only. Not visible to customer.
Digital Input 5 | NA | BIT | NA | NA | Coil Status | 20005 | 1 | Internal Only. Not visible to customer.
Digital Input 6 | NA | BIT | NA | NA | Coil Status | 20006 | 1 | Internal Only. Not visible to customer.
Digital Input 7 | NA | BIT | NA | NA | Coil Status | 20007 | 1 | Internal Only. Not visible to customer.
Digital Input 8 | NA | BIT | NA | NA | Coil Status | 20008 | 1 | Internal Only. Not visible to customer.
Digital Output 1 | NA | BIT | NA | NA | Coil Status | 30001 | 1 | Internal Only. Not visible to customer.
Digital Output 2 | NA | BIT | NA | NA | Coil Status | 30002 | 1 | Internal Only. Not visible to customer.
Digital Output 3 | NA | BIT | NA | NA | Coil Status | 30003 | 1 | Internal Only. Not visible to customer.
Digital Output 4 | NA | BIT | NA | NA | Coil Status | 30004 | 1 | Internal Only. Not visible to customer.
Digital Output 5 | NA | BIT | NA | NA | Coil Status | 30005 | 1 | Internal Only. Not visible to customer.
Digital Output 6 | NA | BIT | NA | NA | Coil Status | 30006 | 1 | Internal Only. Not visible to customer.
Test Mode | NA | BIT | NA | NA | Coil Status | 40001 | 1 | Internal Only. Not visible to customer.
LED 1 | NA | BIT | NA | NA | Coil Status | 60001 | 1 | Internal Only. Not visible to customer.
LED 2 | NA | BIT | NA | NA | Coil Status | 60002 | 1 | Internal Only. Not visible to customer.
LED 3 | NA | BIT | NA | NA | Coil Status | 60003 | 1 | Internal Only. Not visible to customer.
LED 4 | NA | BIT | NA | NA | Coil Status | 60004 | 1 | Internal Only. Not visible to customer.
LED 5 | NA | BIT | NA | NA | Coil Status | 60005 | 1 | Internal Only. Not visible to customer.
LED 6 | NA | BIT | NA | NA | Coil Status | 60006 | 1 | Internal Only. Not visible to customer.
LED 7 | NA | BIT | NA | NA | Coil Status | 60007 | 1 | Internal Only. Not visible to customer.
LED 8 | NA | BIT | NA | NA | Coil Status | 60008 | 1 | Internal Only. Not visible to customer.
Parameters | Units of | Data Type | Size in byte | Conversion | Type of Register | Modbus | No. of | Remarks
| Measurement | (Float/Hex etc.) |  | Multiplier to read the data |  | Register Address | Registers required
WRITE SINGLE COIL STATUS (Function Code: 0x05)
Digital Output 1 | NA | BIT | NA | NA | Coil Status | 30001 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
Digital Output 2 | NA | BIT | NA | NA | Coil Status | 30002 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
Digital Output 3 | NA | BIT | NA | NA | Coil Status | 30003 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
Digital Output 4 | NA | BIT | NA | NA | Coil Status | 30004 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
Digital Output 5 | NA | BIT | NA | NA | Coil Status | 30005 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
Digital Output 6 | NA | BIT | NA | NA | Coil Status | 30006 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
Test Mode | NA | BIT | NA | NA | Coil Status | 40001 | 1 | Internal Only. Not visible to customer.
Restart Controller | NA | BIT | NA | NA | Coil Status | 45001 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
LED 1 | NA | BIT | NA | NA | Coil Status | 60001 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
LED 2 | NA | BIT | NA | NA | Coil Status | 60002 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
LED 3 | NA | BIT | NA | NA | Coil Status | 60003 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
LED 4 | NA | BIT | NA | NA | Coil Status | 60004 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
LED 5 | NA | BIT | NA | NA | Coil Status | 60005 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
LED 6 | NA | BIT | NA | NA | Coil Status | 60006 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
LED 7 | NA | BIT | NA | NA | Coil Status | 60007 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
LED 8 | NA | BIT | NA | NA | Coil Status | 60008 | 1 | Internal Only. Not visible to customer. Only settable when test mode enabled
Parameters | Units of | Data Type | Size in byte | Conversion | Type of Register | Modbus | No. of | Remarks
| Measurement | (Float/Hex etc.) |  | Multiplier to read the data |  | Register Address | Registers required
WRITE MULTIPLE HOLDING REGISTERS (0x10)
Disable Load On Grid Duration Remaining | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 6001 | 2 | Number of seconds till Load Can't be put on Grid
Disable Load On Solar Duration Remaining | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 16001 | 2 | Number of seconds till Load Can't be put on Solar
Mains Under Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30001 | 2
Mains Over Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30003 | 2
Mains Under Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30005 | 2
Mains Over Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30007 | 2
Mains Fail Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30009 | 2
Mains Return Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30011 | 2
Solar Under Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30013 | 2
Solar Over Voltage Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30015 | 2
Solar Under Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30017 | 2
Solar Over Voltage Reset Setting | Volts | Unsigned Integer | 4 | 1 | Holding Register | 30019 | 2
Solar Fail Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30021 | 2
Solar Return Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30023 | 2
Fan Under Current Setting | Milli Ampere | Unsigned Integer | 4 | 1 | Holding Register | 30025 | 2
Fan Over Current Setting | Milli Ampere | Unsigned Integer | 4 | 1 | Holding Register | 30027 | 2
Over Temperature Setting | Celsius | Unsigned Integer | 4 | 1 | Holding Register | 30029 | 2
Under Temperature Setting | Celsius | Unsigned Integer | 4 | 1 | Holding Register | 30031 | 2
Over Temperature Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30033 | 2
Under Temperature Delay Setting | Seconds | Unsigned Integer | 4 | 1 | Holding Register | 30035 | 2
DG Detection Enable/Disable Setting | NA | Unsigned Integer | 4 | 1 | Holding Register | 30037 | 2 | 0: OFF (DG Detection Enabled), 1: ON (DG Detection Disabled)
Fan Disable Setting | NA | Unsigned Integer | 4 | 1 | Holding Register | 30039 | 2 | 0: OFF (Fans Enabled), 1: ON (Fans Disabled)
Firmware Upgrade Status | NA | Unsigned Integer | 4 | 1 | Holding Register | 40001 | 2 | 0: No Action, 1:Signals start of Firmware Uploading, 2: Signals end of Firmware Uploading
Serial Number Lower Half | NA | Unsigned Integer | 4 | 1 | Holding Register | 50003 | 2 | Internal Only. Not visible to customer. Only writtable when test mode enabled. Only writtable together with Serial Number Upper Half
Serial Number Upper Half | NA | Unsigned Integer | 4 | 1 | Holding Register | 50005 | 2 | Internal Only. Not visible to customer. Only writtable when test mode enabled. Only writtable together with Serial Number Lower Half
Functionally Tested | NA | Unsigned Integer | 4 | 1 | Holding Register | 50009 | 2 | Internal Only. Not visible to customer. If set to non-zero, indicates product was tested functionally during production. Only writtable when test mode enabled. Suggested to write the Unix Timestamp for the time when the product was functionally tested.
Calibrated | NA | Unsigned Integer | 4 | 1 | Holding Register | 50011 | 2 | Internal Only. Not visible to customer. If set to non-zero, indicates product was calibrated during production. Only writtable when test mode enabled. Suggested to write Unix Epoch Timestamp of the time when calibration took place
Advance Calibration State | NA | Unsigned Integer | 4 | 1 | Holding Register | 50013 | 2 | Internal Only. Not visible to customer. If set to non-zero, it advances the calibration state machine when it is waiting for external input. Only writtable when test mode enabled.
Scratch Pad | NA | Unsigned Integer | 4 | 1 | Holding Register | 50015 | 2 | Internal Only. Not visible to customer. Used to store a temporarily value. Resets when SOCO restarts on POR.

## EMS Testing Firmware
Controller: | EMS (Energy Management System)
Firmware | Panel Test Firmware V1.00
Protocol | Modbus RTU (RS485)
Addresses | 1-Based Addressing
RS485 Port of EMS | Port 1
Parameters | Units of | Data Type | Size in byte | Conversion | Type of Register | Modbus | No. of | Remarks
| Measurement | (Float/Hex etc.) |  | Multiplier to read the data |  | Register Address | Registers required
READ MULTIPLE HOLDING REGISTERS (Function Code: 0x03)
Temperature Sensor 1 | Celsius | Float | 4 | 1 | Holding Register | 65001 | 2 | Temperature sensor #1 reading
Temperature Sensor 2 | Celsius | Float | 4 | 1 | Holding Register | 65003 | 2 | Temperature sensor #2 reading
Battery Voltage | Volts | Float | 4 | 1 | Holding Register | 65005 | 2 | 48VDC Battery voltage (Analog Input 1)
LAN Connectivity Status | NA | Unsigned Integer | 4 | 1 | Holding Register | 65007 | 2 | 0: Disconnected, 1: Connected
Digital Input 1 | NA | Unsigned Integer | 4 | 1 | Holding Register | 65009 | 2 | 0: Inactive, 1: Active
Digital Input 2 | NA | Unsigned Integer | 4 | 1 | Holding Register | 65011 | 2 | 0: Inactive, 1: Active
Digital Input 3 | NA | Unsigned Integer | 4 | 1 | Holding Register | 65013 | 2 | 0: Inactive, 1: Active
Digital Input 4 | NA | Unsigned Integer | 4 | 1 | Holding Register | 65015 | 2 | 0: Inactive, 1: Active
NOTES (Panel Test Firmware Behaviour)
1. EMS Serial parameters are (baud rate: 9600, parity: No parity, stop bits: 1, slave ID: 1). These are same as the default modbus parameters for SOCO.
2. The customer Modbus master connects to the RS-485 port 1 of the EMS. The EMS in turn talks to SOCO over its RS-485 port 2. Only the port 1 is exposed externally for panel testing.
3. EMS routes incoming requests on a per-address basis: holding registers in the 65001-65016 range listed above are answered locally by the EMS (panel test firmware). Every other request - regardless of function code (0x01 Read Coils, 0x02 Read Discrete Inputs, 0x03 Read Holding Registers outside 65001-65016, 0x05 Write Single Coil, 0x06 Write Single Holding Register, 0x10 Write Multiple Holding Registers, etc.) - is forwarded transparently to SOCO and the SOCO response is relayed back to the master.
4. The EMS-local register block (65001-65016) was chosen to sit above the highest SOCO Modbus address currently in use while still fitting inside the Modbus 16-bit address space (maximum 1-based address = 65536, since the on-the-wire address field is 2 bytes). This leaves clear separation from SOCO and still keeps every byte of every frame within the standard.
5. All EMS-local entries are exposed only via Function Code 0x03 (Read Multiple Holding Registers). Writes to 65001-65016 will be rejected with Modbus exception 0x02 (Illegal Data Address).
6. Float values use IEEE-754 32-bit, transmitted high-word first (big-endian word order), matching the SOCO convention. The two Modbus registers must be read together in a single request.
7. Boolean values (Digital Input 1-4, LAN Connectivity Status) are encoded as 32-bit unsigned integers in the same 2-register format. Only the LSB carries information: 0 = inactive/disconnected, 1 = active/connected. All other bits are reserved and read as 0.
8. The Digital Inputs reflect the raw electrical state of the EMS DI pins after debouncing; their mapping to panel signals is defined by the panel wiring drawing.
9. The 'LAN Connectivity Status' bit is set when the Ethernet PHY reports link-up AND a valid IPv4 address has been acquired (static or DHCP). It is cleared on link-down or IP loss.