SOCO — Load Status Decision Tree

Grid — Decision Tree

Is K5 closed?  (Input Status Register 5)
├─ YES ─ Is K5 stuck closed?  (Input Status Register 610)
│        ├─ NO  → G1  Load On Grid – Grid R Phase Healthy (Input Status Register 801) 
│        └─ YES → G2  Load On Grid — Load On Grid Contactor Stuck Closed (Input Status Register 810)
└─ NO ── Is Grid disabled by user?  (Input Status Register 802)
         ├─ YES → G3  Load Not On Grid — Disabled By User (Input Status Register 811)
         └─ NO ─ Is Grid R Phase Unhealthy?  (Input Status Register 319)
                 ├─ YES → G4  Load Not On Grid — Grid R Phase Unhealthy (Input Status Register 803)
                 └─ NO ─ Is K4 stuck closed?  (Input Status Register 608)
                         ├─ YES → G5  Load Not On Grid — Load On Solar Contactor Stuck Closed (Input Status Register 804)
                         └─ NO ─ Is K5 stuck open?  (Input Status Register 609)
                                 ├─ YES → G6  Load Not On Grid — Load On Grid Contactor Stuck Open (Input Status Register 812)
                                 └─ NO  → G7  Load Not On Grid — Transient (Input Status Register 813)

Grid — Status Table

Checked top to bottom; the first row that has it’s conditions set to TRUE has corresponding status register set to TRUE, rest are set as FALSE. Exactly one is always active. Addresses aren’t in order due to backward compatibility.

| Flag | Status | Active when | Modbus Address |
| --- | --- | --- | --- |
| G1 | Load On Grid – Grid R Phase Healthy | K5 ON AND NOT (K5 Stuck Closed) | 801 |
| G2 | Load On Grid — Load On Grid Contactor Stuck Closed | K5 ON AND (K5 Stuck Closed) | 810 |
| G3 | Load Not On Grid — Disabled By User | NOT (K5 ON) AND (Disable Load On Grid > 0) | 811 |
| G4 | Load Not On Grid — Grid R Phase Unhealthy | NOT (K5 ON) AND NOT (Disable Load On Grid > 0) AND (Grid R Phase Unhealthy) | 803 |
| G5 | Load Not On Grid — Load On Solar Contactor Stuck Closed | NOT (K5 ON) AND NOT (Disable Load On Grid > 0) AND NOT (Grid R Phase Unhealthy) AND (K4 Stuck Closed) | 804 |
| G6 | Load Not On Grid — Load On Grid Contactor Stuck Open | NOT (K5 ON) AND NOT (Disable Load On Grid > 0) AND NOT (Grid R Phase Unhealthy) AND NOT (K4 Stuck Closed) AND (K5 Stuck Open) | 812 |
| G7 | Load Not On Grid — Transient | NOT (K5 ON) AND NOT (Disable Load On Grid > 0) AND NOT (Grid R Phase Unhealthy) AND NOT (K4 Stuck Closed) AND NOT (K5 Stuck Open) | 813 |

Solar — Decision Tree

Is Load on solar?  (Input Status Register 4 AND 6 — K4 and K6 closed)
├─ YES ─ Is K4 or K6 stuck closed?  (Input Status Register 608 OR 612)
│        ├─ NO  → S1  Load On Solar – Solar R Phase Healthy (Input Status Register 805)
│        └─ YES → S2  Load On Solar — Solar Contactor(s) Stuck Closed (Input Status Register 814)
└─ NO ── Is Grid contactors stuck closed?  (Input Status Register 602 OR 604 OR 606 OR 610)
         ├─ YES → S7  Load Not On Solar — Grid Contactor(s) Stuck Closed (Input Status Register 816)
         └─ NO ─ Is Grid available?  (Input Status Register NOT 319 AND NOT 802)
                 ├─ YES → S3  Load Not On Solar — Grid Available (Input Status Register 808)
                 └─ NO ─ Is Solar disabled by user?  (Input Status Register 806)
                         ├─ YES → S4  Load Not On Solar — Load On Solar Disabled By User (Input Status Register 815)
                         └─ NO ─ Is Solar R Phase Unhealthy?  (Input Status Register 322)
                                 ├─ YES → S5  Load Not On Solar — Solar R Phase Unhealthy (Input Status Register 807)
                                 └─ NO ─ Is DG running?  (Input Register NOT 7 AND Holding Register 30037 == 0)
                                         ├─ YES → S6  Load Not On Solar — DG Running (Input Status Register 809)
                                         └─ NO ─ Is K4/K6 stuck open?  (Input Status Register 607 OR 611)
                                                 ├─ YES → S8  Load Not On Solar — Solar Contactor(s) Stuck Open (Input Status Register 817)
                                                 └─ NO  → S9  Load Not On Solar — Transient (Input Status Register 818)

Solar — Status Table

Checked top to bottom; the first row that has it’s conditions set to TRUE has corresponding status register set to TRUE, rest are set as FALSE. Exactly one is always active. Addresses aren’t in order due to backward compatibility.

| Flag | Status | Active when | Modbus Address |
| --- | --- | --- | --- |
| S1 | Load On Solar – Solar R Phase Healthy | (K4 ON AND K6 ON) AND NOT (K4 OR K6 Stuck Closed) | 805 |
| S2 | Load On Solar — Solar Contactor(s) Stuck Closed | (K4 ON AND K6 ON) AND (K4 OR K6 Stuck Closed) | 814 |
| S3 | Load Not On Solar — Grid Available | NOT (K4 ON AND K6 ON) AND NOT (K1 OR K2 OR K3 OR K5 Stuck Closed) AND NOT (Grid R Phase Unhealthy) AND NOT (Disable Load On Grid > 0) | 808 |
| S4 | Load Not On Solar — Load On Solar Disabled By User | NOT (K4 ON AND K6 ON) AND NOT (K1 OR K2 OR K3 OR K5 Stuck Closed) AND (Grid R Phase Unhealthy OR Disable Load On Grid > 0) AND (Disable Load On Solar > 0) | 815 |
| S5 | Load Not On Solar — Solar R Phase Unhealthy | NOT (K4 ON AND K6 ON) AND NOT (K1 OR K2 OR K3 OR K5 Stuck Closed) AND (Grid R Phase Unhealthy OR Disable Load On Grid > 0) AND NOT (Disable Load On Solar > 0) AND (Solar R Phase Unhealthy) | 807 |
| S6 | Load Not On Solar — DG Running | NOT (K4 ON AND K6 ON) AND NOT (K1 OR K2 OR K3 OR K5 Stuck Closed) AND (Grid R Phase Unhealthy OR Disable Load On Grid > 0) AND NOT (Disable Load On Solar > 0) AND NOT (Solar R Phase Unhealthy) AND (NOT (DG Off) AND DG Detection Enabled) | 809 |
| S7 | Load Not On Solar — Grid Contactor(s) Stuck Closed | NOT (K4 ON AND K6 ON) AND (K1 OR K2 OR K3 OR K5 Stuck Closed) | 816 |
| S8 | Load Not On Solar — Solar Contactor(s) Stuck Open | NOT (K4 ON AND K6 ON) AND NOT (K1 OR K2 OR K3 OR K5 Stuck Closed) AND (Grid R Phase Unhealthy OR Disable Load On Grid > 0) AND NOT (Disable Load On Solar > 0) AND NOT (Solar R Phase Unhealthy) AND (DG Off OR DG Detection Disabled) AND (K4 OR K6 Stuck Open) | 817 |
| S9 | Load Not On Solar — Transient | NOT (K4 ON AND K6 ON) AND NOT (K1 OR K2 OR K3 OR K5 Stuck Closed) AND (Grid R Phase Unhealthy OR Disable Load On Grid > 0) AND NOT (Disable Load On Solar > 0) AND NOT (Solar R Phase Unhealthy) AND (DG Off OR DG Detection Disabled) AND NOT (K4 OR K6 Stuck Open) | 818 |

Independent Status Registers

802  —  Grid Disabled By User:  TRUE when Disable Load On Grid (Holding Register 6001) > 0.

806  —  Solar Disabled By User:  TRUE when Disable Load On Solar (Holding Register 16001) > 0.